Confined Space Pre-Entry Inspection Checklist

| Date: |  | Entry Supervisor: |  |
| --- | --- | --- | --- |
| Space ID/Name: |  | Location: |  |
| Purpose of Entry: |  | Permit #: |  |
| Rescue Service: |  | Contact Phone: |  |

Part 1: Atmospheric Testing (test in order listed)

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Oxygen (O₂) — Acceptable range: 19.5%–23.5%; record reading: _____ % |  |  |
| 2 | Combustible Gases (LEL) — Below 10% of Lower Explosive Limit; record reading: _____ % LEL |  |  |
| 3 | Hydrogen Sulfide (H₂S) — Below 10 ppm (TWA PEL); record reading: _____ ppm |  |  |
| 4 | Carbon Monoxide (CO) — Below 50 ppm (TWA PEL); record reading: _____ ppm |  |  |
| 5 | Other Toxic Substances — Below applicable PEL; substance: ____________ reading: _____ |  |  |
| 6 | Gas Monitor Calibration — Bump tested today; calibration current per manufacturer schedule; sensors not expired |  |  |

Part 2: Hazard Controls and Isolation

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Energy Isolation (LOTO) — All energy sources locked out/tagged out per 1910.147; electrical, mechanical, hydraulic, pneumatic, chemical, thermal |  |  |
| 2 | Line Breaking/Blanking — Pipes and lines disconnected, blanked, blinded, or double-blocked and bled; no gravity feed pathways open |  |  |
| 3 | Ventilation — Mechanical ventilation in place and operating; clean air source; continuous during entry; ductwork reaches all areas |  |  |
| 4 | Inerting/Purging — If previously inerted, atmosphere restored to breathable levels; purge procedures completed and documented |  |  |
| 5 | Physical Hazards — Engulfment hazards controlled; moving parts secured; fall hazards addressed; hot surfaces guarded or cooled |  |  |
| 6 | Barriers and Signage — Space posted with "DANGER — Permit-Required Confined Space"; unauthorized entry prevented |  |  |

Part 3: Equipment Inspection

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Gas Monitors — Calibrated and bump-tested; alarms set correctly; battery charged; functioning in fresh air |  |  |
| 2 | Ventilation Equipment — Blower/fan operational; ductwork intact; adequate CFM for space volume; power supply reliable |  |  |
| 3 | Retrieval System — Tripod/davit arm stable and rated; winch functions properly; retrieval line in good condition; harness inspected |  |  |
| 4 | Communication Equipment — Radios or hardwired communication tested between entrant, attendant, and entry supervisor |  |  |
| 5 | Respiratory Protection — SCBA or supplied-air respirator inspected, tested, and fit-checked if required; air supply adequate |  |  |
| 6 | Lighting — Explosion-proof or intrinsically safe for the atmosphere; adequate illumination for the work |  |  |
| 7 | PPE — Hard hat, safety glasses, gloves, protective clothing appropriate for identified hazards |  |  |

Part 4: Personnel and Rescue Readiness

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Entry Supervisor — On site, authorized to issue permits, knows hazards, can cancel permit if conditions change |  |  |
| 2 | Authorized Entrants — All trained per 1910.146(g); know hazards, exposure symptoms, equipment use, and alerting procedures |  |  |
| 3 | Attendant — Stationed outside space; knows hazards; maintains entrant count; will not enter for rescue; can order evacuation |  |  |
| 4 | Rescue Service — Identified and available; on-site team has practiced within 12 months; off-site response time evaluated as timely |  |  |
| 5 | Training Currency — All personnel training current; no changes in duties or hazards since last training |  |  |

Deficiencies Found

| # | Description | Corrective Action | Assigned To | Date Fixed |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

WARNING: NEVER enter a confined space to attempt rescue without proper training, equipment, and atmospheric monitoring. Approximately 60% of confined space fatalities are would-be rescuers. If conditions change during entry, evacuate immediately and reassess.

Entry Authorized:   □ Yes    □ No — Reason: ________________________________________

Entry Supervisor: ________________________________________    Date: ______________

Safety Manager: ________________________________________    Date: ______________

Provided by Ecesis EHS Software – www.ecesis.net