Emergency Exit & Egress Inspection Checklist

| Date: |  |
| --- | --- |
| Inspector: |  |
| Building/Location: |  |
| Floor/Area: |  |
| Inspection Type: | Monthly / Quarterly / Annual |
| Total Exits Inspected: |  |

Part 1: Exit Signage & Marking

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| EXIT sign present at each exit, letters at least 6 inches high per OSHA 1910.37(b)(7) | ☐ OK ☐ Fail ☐ N/A |
| EXIT signs continuously illuminated (internal, external, or self-luminous) with battery backup | ☐ OK ☐ Fail ☐ N/A |
| Directional signs posted where path to exit is not immediately apparent per 1910.37(b)(4) | ☐ OK ☐ Fail ☐ N/A |
| Doorways that could be mistaken for exits marked "Not an Exit" or with actual use per 1910.37(b)(5) | ☐ OK ☐ Fail ☐ N/A |
| Line-of-sight to exit signs unobstructed by decorations, banners, equipment, or inventory | ☐ OK ☐ Fail ☐ N/A |

Part 2: Exit Doors & Hardware

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| Exit doors open freely without keys, tools, or special knowledge from inside per 1910.36(d)(1) | ☐ OK ☐ Fail ☐ N/A |
| Doors swing outward in direction of travel for rooms with 50+ occupants or high-hazard areas | ☐ OK ☐ Fail ☐ N/A |
| Self-closing fire doors functional and not propped open (unless alarm-connected hold-open devices) | ☐ OK ☐ Fail ☐ N/A |
| Door hardware (hinges, panic bars, closers) in good condition and properly aligned | ☐ OK ☐ Fail ☐ N/A |
| Exit doors not locked, chained, or secured from inside during occupied hours | ☐ OK ☐ Fail ☐ N/A |

Part 3: Exit Route Clearance & Condition

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| Exit routes completely free and unobstructed (no materials, equipment, or storage) per 1910.37(a)(1) | ☐ OK ☐ Fail ☐ N/A |
| Exit route width at least 28 inches at narrowest point per 1910.36(g)(2) | ☐ OK ☐ Fail ☐ N/A |
| Ceiling height at least 7 feet 6 inches; projections not lower than 6 feet 8 inches per 1910.36(g)(1) | ☐ OK ☐ Fail ☐ N/A |
| Floor surfaces in good repair (no holes, loose tiles, wet/slippery areas, trip hazards) | ☐ OK ☐ Fail ☐ N/A |
| Continuous uninterrupted path from occupied areas to exit discharge; no dead-end violations | ☐ OK ☐ Fail ☐ N/A |
| At least two exit routes available and located as far apart as practical per 1910.36(b)(2) | ☐ OK ☐ Fail ☐ N/A |

Part 4: Exit Lighting & Alarm Systems

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| Exit routes adequately lighted (min. 1 footcandle) per 1910.37(b)(1); no dark areas | ☐ OK ☐ Fail ☐ N/A |
| Emergency lighting activates on power failure and provides adequate illumination | ☐ OK ☐ Fail ☐ N/A |
| Stairwell lighting adequate at all landings and treads | ☐ OK ☐ Fail ☐ N/A |
| Employee alarm system operable with distinctive signal per 1910.37(e) and 1910.165 | ☐ OK ☐ Fail ☐ N/A |

⚠ WARNING: If any exit door is locked, blocked, or inoperable during occupied hours, correct immediately. Blocked or locked exits are life safety hazards that can result in fatalities during emergencies.

Deficiency Log

| # | Deficiency Description | Corrective Action | Target Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

| Inspector Signature | Date |
| --- | --- |

| Facility Manager Signature | Date |
| --- | --- |