Emergency Lighting Inspection Checklist

| Date: |  | Inspector: |  |
| --- | --- | --- | --- |
| Building/Location: |  | Floor/Area: |  |
| Inspection Type: |  | Total Units Inspected: |  |

Part 1: Monthly Visual Inspection

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Emergency Light Units — Charge indicator light is on; no visible damage to housing, lens, or lamp heads; aimed correctly; not obstructed |  |  |
| 2 | Exit Signs — Illuminated and visible from all required directions; all letters legible; no cracked or missing lenses; arrows correct |  |  |
| 3 | Combination Units — Both exit sign face and emergency lamp heads functional; charge indicator on; no damage |  |  |
| 4 | Self-Testing Units — Status indicator shows no errors from most recent self-test; no visible damage; no fault codes displayed |  |  |
| 5 | Mounting and Installation — All units securely mounted; no loose fixtures or hanging wires; mounting height appropriate for visibility |  |  |

Part 2: Monthly 30-Second Functional Test

| # | Inspection Item | OK | Fail |
| --- | --- | --- | --- |
| 1 | Test Activation — Test button pressed and held for at least 30 seconds (or AC power disconnected to circuit) |  |  |
| 2 | Lamp Operation — All lamp heads illuminate on battery power; adequate brightness; no flickering or dimming; LEDs fully lit |  |  |
| 3 | Exit Sign Illumination — Exit sign remains illuminated on battery; all letters and arrows visible; no significant dimming |  |  |
| 4 | Transfer Time — Transfer to battery power occurs within 10 seconds of AC power loss |  |  |
| 5 | Power Restore — Unit returns to normal operation; charge indicator re-illuminates confirming battery charging resumed |  |  |

Part 3: Annual 90-Minute Duration Test

| # | Inspection Item | OK | Fail | N/A |
| --- | --- | --- | --- | --- |
| 1 | Preparation — Coordinated with building management; scheduled during low-occupancy; occupants notified in advance |  |  |  |
| 2 | AC Power Disconnected — Circuit breaker(s) turned off; all battery-powered units activated automatically |  |  |  |
| 3 | 90-Minute Monitoring — All units remain illuminated for the full 90 minutes; time of any unit failure recorded |  |  |  |
| 4 | Illumination Quality — Egress path lighting adequate throughout test; initial ≥1 fc avg; ≥0.6 fc avg at 90 min |  |  |  |
| 5 | Power Restored and Verified — AC power restored; all charge indicators re-illuminate; failed units noted for replacement |  |  |  |
| 6 | Results Documented — Each unit identified by location/ID; pass/fail recorded; corrective actions scheduled for deficiencies |  |  |  |

Deficiencies Found

| # | Description | Corrective Action | Assigned To | Date Fixed |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

WARNING: Any emergency lighting unit that fails to illuminate on battery power or does not sustain illumination for the required test duration must be repaired or replaced immediately. Non-functional emergency lighting during an actual emergency can prevent safe evacuation and endanger lives.

Units Passed: ______    Units Failed: ______    Overall Result:  □ Pass    □ Fail (corrective actions required)

Inspector: ________________________________________    Date: ______________

Facility Manager: ________________________________________    Date: ______________

Provided by Ecesis EHS Software – www.ecesis.net