FIRE ALARM SYSTEM INSPECTION CHECKLIST

Per NFPA 72 Chapter 14

| Date: _______________ | Inspector: _________________________ |
| --- | --- |
| Building / Location: _________________________ | FACP Make / Model: _________________________ |
| System Type: ☐ Addressable ☐ Conventional | Monitoring Company: _________________________ |
| Inspection Type: ☐ Monthly ☐ Semiannual ☐ Annual | Monitoring Company Notified: ☐ Yes ☐ No |
| Fire Dept. Notified: ☐ Yes ☐ No | Occupants Notified: ☐ Yes ☐ No |

WARNING: Notify all affected parties before testing: monitoring company, fire department, building occupants, and the authority having jurisdiction (AHJ).

Part 1: Fire Alarm Control Panel (FACP)

| # | Inspection Item | OK | Fail | Notes |
| --- | --- | --- | --- | --- |
| 1 | System in normal operating condition — no trouble/alarm signals |  |  |  |
| 2 | Primary (AC) power connected and operating |  |  |  |
| 3 | Secondary (battery) power transfer verified |  |  |  |
| 4 | All LEDs and indicator lights showing normal status |  |  |  |
| 5 | Panel enclosure intact, door closes and latches |  |  |  |
| 6 | As-built drawings and zone maps present at panel |  |  |  |

Part 2: Initiating Devices

| # | Inspection Item | OK | Fail | Notes |
| --- | --- | --- | --- | --- |
| 1 | Smoke detectors — not painted, obstructed, or damaged |  |  |  |
| 2 | Smoke detectors — functional test (activate with listed method) |  |  |  |
| 3 | Heat detectors — no paint, damage, or obstruction |  |  |  |
| 4 | Heat detectors — functional test per manufacturer instructions |  |  |  |
| 5 | Duct smoke detectors — sampling tubes clear, airflow adequate |  |  |  |
| 6 | Duct smoke detectors — functional test, verify HVAC shutdown |  |  |  |
| 7 | Manual pull stations — accessible, visible, not obstructed |  |  |  |
| 8 | Manual pull stations — trip and verify alarm at FACP |  |  |  |
| 9 | Waterflow switches — test at inspector’s test connection |  |  |  |
| 10 | Tamper/supervisory switches — turn 2 revolutions, verify signal |  |  |  |

Part 3: Notification Appliances

| # | Inspection Item | OK | Fail | Notes |
| --- | --- | --- | --- | --- |
| 1 | Audible devices (horns/speakers) — present, not damaged |  |  |  |
| 2 | Audible devices — activate and verify adequate sound level |  |  |  |
| 3 | Visual devices (strobes) — lenses not painted or obscured |  |  |  |
| 4 | Visual devices — activate and verify flash pattern |  |  |  |
| 5 | Speaker/voice systems — test voice intelligibility (if equipped) |  |  |  |

Part 4: Secondary Power (Batteries)

| # | Inspection Item | OK / Fail | Notes |
| --- | --- | --- | --- |
| 1 | Battery visual — no corrosion, leakage, or swelling |  |  |
| 2 | Battery connections tight and clean |  |  |
| 3 | Battery manufacture date recorded (replace sealed lead-acid every 4 years) |  |  |
| 4 | Battery voltage test — not below 2.05V per cell under load |  |  |
| 5 | Battery load/discharge test (annual) — system operates on battery power |  |  |

Deficiencies Found

| # | Location / ID | Deficiency Description | Corrective Action | Due Date |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

Testing Summary

| Device Type | Total Tested | Total Failed |
| --- | --- | --- |
| Smoke Detectors |  |  |
| Heat Detectors |  |  |
| Pull Stations |  |  |
| Notification Appliances |  |  |
| Other Devices |  |  |

WARNING: Any device that fails functional testing must be repaired or replaced. System impairments must be reported to the AHJ and monitoring company. Implement a fire watch if the system cannot be restored to normal operation within 4 hours.

Inspector / Technician Signature                                                    Date: _______________

Facility Manager Signature                                                    Date: _______________