Fire Extinguisher Inspection Checklist

| Date: |  |
| --- | --- |
| Inspector: |  |
| Building/Location: |  |
| Extinguisher Type: | ABC / BC / CO₂ / Class K / Water / Clean Agent |
| Extinguisher ID/Tag #: |  |
| Inspection Type: | Monthly / Annual / 6-Year / Hydrostatic |

Part 1: Monthly Visual Inspection

| Inspection Item | Frequency | Status |
| --- | --- | --- |
| Extinguisher in designated location per floor plan | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Not blocked, hidden, or obstructed; signage visible | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Mounting height correct (top handle ≤5 ft for ≤40 lb units; ≤3.5 ft for heavier) | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Pressure gauge in operable (green) range | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Pull pin in place and not bent or corroded | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Tamper seal intact and not broken | Monthly | ☐ OK ☐ Fail ☐ N/A |
| No dents, corrosion, leaks, or physical damage to cylinder | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Hose and nozzle free of cracks, blockage, deterioration | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Operating instructions legible and facing outward | Monthly | ☐ OK ☐ Fail ☐ N/A |
| CO₂ units: weighed; within nameplate tolerance | Monthly | ☐ OK ☐ Fail ☐ N/A |
| Inspection tag current with date and initials | Monthly | ☐ OK ☐ Fail ☐ N/A |

Part 2: Annual Maintenance (Certified Technician)

| Inspection Item | Frequency | Status |
| --- | --- | --- |
| Thorough external examination: cylinder, valve, handle, bracket | Annual | ☐ OK ☐ Fail ☐ N/A |
| Mechanical parts: handle, levers, locking mechanisms operate freely | Annual | ☐ OK ☐ Fail ☐ N/A |
| Pull pin removes without excessive force | Annual | ☐ OK ☐ Fail ☐ N/A |
| Valve stem, O-rings, and pressure relief device in good condition | Annual | ☐ OK ☐ Fail ☐ N/A |
| Agent type, amount, and condition verified per nameplate | Annual | ☐ OK ☐ Fail ☐ N/A |
| Hose connections secure; gaskets in good condition | Annual | ☐ OK ☐ Fail ☐ N/A |
| Nozzle/horn clear of obstruction and properly attached | Annual | ☐ OK ☐ Fail ☐ N/A |
| UL/FM listing label present and legible | Annual | ☐ OK ☐ Fail ☐ N/A |
| Rating matches hazard classification of the area | Annual | ☐ OK ☐ Fail ☐ N/A |
| New annual service tag attached with date and technician | Annual | ☐ OK ☐ Fail ☐ N/A |

Part 3: 6-Year Internal Examination & Hydrostatic Testing

| Inspection Item | Frequency | Status |
| --- | --- | --- |
| Stored-pressure unit emptied and internal exam completed | 6-Year | ☐ OK ☐ Fail ☐ N/A |
| Cylinder interior: no corrosion, pitting, or thread damage | 6-Year | ☐ OK ☐ Fail ☐ N/A |
| Valve assembly disassembled, inspected, and rebuilt | 6-Year | ☐ OK ☐ Fail ☐ N/A |
| Verification-of-service collar installed at cylinder neck | 6-Year | ☐ OK ☐ Fail ☐ N/A |
| Hydrostatic test completed at required pressure (5-yr or 12-yr) | 5/12-Year | ☐ OK ☐ Fail ☐ N/A |
| No permanent expansion, distortion, leakage, or defects | 5/12-Year | ☐ OK ☐ Fail ☐ N/A |
| Cylinder marked with test date, pressure, and testing agency | 5/12-Year | ☐ OK ☐ Fail ☐ N/A |
| Recharged with correct agent and repressurized | After service | ☐ OK ☐ Fail ☐ N/A |

⚠ CONDEMNED EXTINGUISHERS: Remove from service immediately any extinguisher with a corroded or damaged shell, repaired by welding/brazing, using an obsolete agent, or missing a current service tag. Replace with a properly rated unit and dispose per local regulations.

Deficiency Log

| # | Deficiency Description | Corrective Action | Target Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

| Inspector/Technician Signature Date | Facility Manager Signature Date |
| --- | --- |