Fire Sprinkler System Inspection Checklist

| Date: |  |
| --- | --- |
| Inspector: |  |
| Building/Location: |  |
| System Type: | Wet / Dry / Pre-Action / Deluge |
| Inspection Type: | Weekly / Monthly / Quarterly / Annual |
| Monitoring Company: |  |

Part 1: Sprinkler Heads & Piping

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| Sprinkler heads free of corrosion, paint, physical damage, and foreign material (annual) | ☐ OK ☐ Fail ☐ N/A |
| No obstructions within 18 inches below sprinkler deflectors (standard spray type) | ☐ OK ☐ Fail ☐ N/A |
| Spare sprinkler supply: minimum 6 of each type/temp rating with wrench for each | ☐ OK ☐ Fail ☐ N/A |
| Piping and fittings: no damage, leaks, corrosion, or misalignment (annual) | ☐ OK ☐ Fail ☐ N/A |
| Hangers and seismic bracing intact, undamaged, and securely attached (annual) | ☐ OK ☐ Fail ☐ N/A |
| Sprinkler head age and replacement schedule tracked (fast-response: 25 yr; standard: 50 yr) | ☐ OK ☐ Fail ☐ N/A |

Part 2: Control Valves & Water Supply

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| All control valves in normal open position, sealed/locked/supervised (weekly/monthly) | ☐ OK ☐ Fail ☐ N/A |
| System gauges within normal operating range (weekly dry/pre-action; monthly wet pipe) | ☐ OK ☐ Fail ☐ N/A |
| Alarm valve condition: clean, no damage, no leaks, trim valves correct (monthly) | ☐ OK ☐ Fail ☐ N/A |
| Main drain test completed; static and residual pressures recorded and compared (quarterly) | ☐ OK ☐ Fail ☐ N/A |
| Fire department connection (FDC) visible, accessible, couplings/caps intact (quarterly) | ☐ OK ☐ Fail ☐ N/A |

Part 3: System-Specific Components

| Inspection Item | OK / Fail / N/A |
| --- | --- |
| Dry pipe valve: gauges normal (weekly); full trip test completed (annual) | ☐ OK ☐ Fail ☐ N/A |
| Pre-action/deluge valves: visual (quarterly); full trip test with detection (annual) | ☐ OK ☐ Fail ☐ N/A |
| Waterflow alarm devices tested; alarm within 90 seconds of sustained flow (semiannual) | ☐ OK ☐ Fail ☐ N/A |
| Antifreeze solution concentration tested before freezing season (annual) | ☐ OK ☐ Fail ☐ N/A |
| Inspector's test connection accessible, functional, and drain piped to safe discharge | ☐ OK ☐ Fail ☐ N/A |

⚠ WARNING: When any sprinkler system or portion is taken out of service, implement a fire watch immediately. Notify alarm monitoring company, fire department, insurance carrier, and building occupants per NFPA 25 Chapter 15.

Deficiency Log

| # | Deficiency Description | Corrective Action | Target Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

| Inspector/Technician Signature | Date |
| --- | --- |

| Facility Manager Signature | Date |
| --- | --- |